Planning, Design & Construction
Campus Facilities

117 General Services Building
Columbia, MO 65211-3200

Construction Management

University of Missouri-Columbia 						
Phone (573) 882-1133

Fax (573) 882-1175

Drawing #:

Tag #:

Project:		
Date:

# AHU CHECKLIST

| ARRIVAL |  |  |  |
| --- | --- | --- | --- |
| Model Verification |  |  |  |
|  | Specified | Submitted | Installed |
| Manufacturer |  |  |  |
| Model |  |  |  |
| S/N |  |  |  |
| Cooling Capacity |  |  |  |
| Heating Capacity |  |  |  |
| Volts/PH/A |  |  |  |

| Item |  | Comment |
| --- | --- | --- |
| AHU free of damage? |  |  |
| Access door latches operable? |  |  |
| Gaskets for access doors OK? |  |  |
| Inspect Demounts for proper reassembly? |  |  |
| All Components (mixing boxes, coils,fans are present and in proper order? |  |  |
| Extended grease lubrication lines installed for each fan? |  |  |
| Protective shroud for belts in place and secure? |  |  |
| Heating/Cooling Coil surfaces free of damage? |  |  |
| Drain Pans Stainless steel? |  |  |
| Adjacent floor drains ready? |  |  |
| Installation and start up manual is on site? |  |  |
| Unit Tags Affixed |  |  |

| Supply fan horsepower |  | Design | Submitted | Installed |
| --- | --- | --- | --- | --- |
| Fan voltage and full load amps. |  | Voltage | Amps |  |
| Fan efficiency design/actual |  | Normal | High | Inverter Duty |

| Return fan horse power |  | Design | Submitted | Installed |
| --- | --- | --- | --- | --- |
| Fan voltage and full load amps. |  | Voltage | Amps |  |
| Fan efficiency design/actual |  | Normal | High | Inverter Duty |

| Concrete pad design/actual |  |  |
| --- | --- | --- |
| Unit Secured as required? |  |  |
| Adequate Clearance around unit for maintenance? |  |  |
| Unit Clean? |  |  |
| Shipping bolts removed? |  |  |
| Drain pan piping install per drawings and primed? |  |  |
| Coil piping matches contract drawings? |  |  |
| Control valves installed correctly? |  |  |
| High point vent installed? |  |  |
| Drains installed and capped? |  |  |
| Piping has been tested and flushed? |  |  |
| Piping insulation completed? Type and thickness as required? |  |  |
| Piping supply and return labeled correctly? |  |  |
| Ductwork installed and tested? |  |  |
| Ductwork insulated? |  |  |
| All dampers and air valves set wide open? |  |  |
| Dampers installed and operate correctly? |  |  |
| Pulleys and belts aligned and tight? |  |  |
| VFD's commissioned? Overloads set at proper value? |  |  |
| Starters commissioned? Overloads the right size? |  |  |
| Motor rotation in proper direction? |  |  |

| Controls installed per plans? |  |  |  |  |
| --- | --- | --- | --- | --- |
| Freeze stat installed and tested? |  | Set point |  |  |
| Static pressure safety installed and tested? |  | Set point |  |  |
| Smoke detectors installed and tested? |  |  |  |  |
| Supply fan amps at 60 hertz |  | FLA | Running |  |
| Return fan amps at 60 hertz |  | FLA | Running |  |
| All controls checked for proper operation and sequence? |  |  |  |  |
| Manufacturers startup checklist completed and attached? |  |  |  |  |
| Final filter change if required. |  |  |  |  |

Inspector Name (print)

Inspector Signature

*Fill out all form fields before signing!

Name		 	Organization			Title			Signature 
 
_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________
 
_________________________________________________________________________________________________________________

_________________University of Missouri Commissioning Authority