# Automatic Transfer Switch Construction Checklist

| Project: |  |
| --- | --- |

| Date: |  |
| --- | --- |
| Building: |  |
| Location: |  |

# Submittal / Approvals

Submittal. The above equipment and systems integral to them are complete and ready for functional testing. The checklist items are complete and have been checked off only by parties having direct knowledge of the event, as marked below, respective to each responsible contractor. This construction checklist is submitted for approval, subject to an attached list of outstanding items yet to be completed. A Statement of Correction will be submitted upon completion of any outstanding areas. None of the outstanding items preclude safe and reliable functional tests being performed.		 List attached.

| Electrical Contractor | Date | Controls Contractor | Date |
| --- | --- | --- | --- |
| Other Party: | Date | General Contractor | Date |

Construction checklist items are to be completed as part of startup & initial checkout, preparatory to performing test procedures.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- If this form is not used for documenting, one of similar rigor shall be used.

- Contractors assigned responsibility for sections of the checklist shall be responsible to see that checklist items by their subcontractors are completed and checked off.

Approvals. This filled-out checklist has been reviewed. Its completion is approved with the exceptions noted below.

| Commissioning Authority | Date | Owner’s Representative | Date |
| --- | --- | --- | --- |

| Panel Information |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Panel Tag |  | Panel Location |  |  |  |  |  |  |  |  |
| System / Equip |  |  | 208-120 or |  | 480-277 |  |  | Normal or |  | Emergency |
| Manufacturer |  | Model Number |  |  |  |  |  |  |  |  |
| Serial Number |  | Short Circuit Capacity |  |  |  |  |  |  |  |  |
| Volts/Phase Rating |  | Amperage Rating |  |  |  |  |  |  |  |  |
| Service Area |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |

| Associated Checklists |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Emergency Generator |  | Panels |  | Other |  |
| Comments: |  |  |  |  |  |

| Requested documentation submitted | Rec’d | Comments |
| --- | --- | --- |
| Manufacturer’s cut sheets |  |  |
| Installation and startup manual and plan |  |  |
| O&M manuals |  |  |
| Factory test results |  |  |
| Sequences and control strategies |  |  |
| Warranty Certificate |  |  |
| Comments: |  |  |

| Distribution Panel Enclosure/Cabinetry |  |  |  |
| --- | --- | --- | --- |
| Check if Acceptable; Provide comment if unacceptable |  | NA | Comment |
| Equipment installed per manufacturer’s instructions and specifications |  |  |  |
| Equipment installed agrees with shop drawings and specifications |  |  |  |
| Verify mounting, location and clearances are per plans and specifications |  |  |  |

| Inspect for physical, electrical and mechanical condition of equipment and cabinet. No damage evident |  |  |  |
| --- | --- | --- | --- |
| Inspect panels and doors for proper fit and alignment |  |  |  |
| Equipment labels permanently affixed |  |  |  |
| Cabinet is clean and clear of dust or dirt |  |  |  |
| Verify the application of manufacturer recommended torque values applied to bolted connections |  |  |  |
| Seismic anchoring installed and functional where applicable (non- short circuiting) |  |  |  |
| Alarm contact is properly installed and wired |  |  |  |
| Communications cable installed and connected |  |  |  |
| Protective relays properly installed and wired (frequency, over/under voltage) |  |  |  |
| Emergency power control system installed, powered and diagnostics performed |  |  |  |
| Inspect insulators, barriers and shields for damage or contamination |  |  |  |
| Verify that enclosure is properly grounded and resistance to ground meets grounding specifications |  |  |  |
| Metering installed, properly sized for desired voltage and amperage ranges and properly wired |  |  |  |
| Inspect mechanical linkage or tie connections – operate switch manually |  |  |  |
| By-pass switch operates correctly in all positions |  |  |  |
| Verify phase relationships |  |  |  |
| ATS is exercised in auto mode without line voltage or loads applied |  |  |  |
| Megger test of switch current carrying components – phase to phase and phase to ground. Test voltage per manufacturer’s recommendations |  |  |  |

| Operational Checks |  |  |  |
| --- | --- | --- | --- |
| Check if Acceptable; Provide comment if unacceptable |  | NA | Comment |
| Specified sequences of operation and operating schedules have been provided with all variations documented |  |  |  |
| Specified point-to-point checks have been completed and documentation record submitted for this system |  |  |  |

# Sensor and Actuator Calibration

All field-installed sensors and gages, and all actuators (dampers and valves) on this piece of equipment shall be calibrated in accordance with Specification Section 01810. All test instruments shall have had a certified calibration within the last 12 months: Y/N	. Sensors installed in the unit at the factory with calibration certification provided need not be field calibrated.

| Sensor or Actuator Tag & Location | Location OK | 1st Gage or BAS Value | Instrument Measured Value | Final Gage or BAS Value | Pass Y / N |
| --- | --- | --- | --- | --- | --- |

Comments:

*Fill out all form fields before signing!

Name		 	Organization			Title			Signature 
 
_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________
 
_________________________________________________________________________________________________________________

_________________University of Missouri Commissioning Authority