# Boiler Construction Checklist

| Project: |  |
| --- | --- |

| Date: |  |
| --- | --- |
| Chiller Tag: |  |
| Building: |  |
| Location: |  |

# Submittal / Approvals

Submittal. The above equipment and systems integral to them are complete and ready for functional testing. The checklist items are complete and have been checked off only by parties having direct  knowledge of the event, as marked below, respective to each responsible contractor. This construction checklist is submitted for approval, subject to an attached list of outstanding items yet to be completed. A Statement of Correction will be submitted upon completion of any outstanding areas. None of the outstanding items preclude safe and reliable functional tests being performed.		 List attached.

| Mechanical Contractor | Date | Controls Contractor | Date |
| --- | --- | --- | --- |
| Electrical Contractor | Date | Sheet Metal Contractor | Date |
| TAB Contractor | Date | General Contractor | Date |

Construction checklist items are to be completed as part of startup & initial checkout, preparatory to performing test procedures.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- If this form is not used for documenting, one of similar rigor shall be used.

- Contractors assigned responsibility for sections of the checklist shall be responsible to see that checklist items by their subcontractors are completed and checked off.

Approvals. This filled-out checklist has been reviewed. Its completion is approved with the exceptions noted below.

| Commissioning Authority | Date | Owner’s Representative | Date |
| --- | --- | --- | --- |

| Boiler 1 Information |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Make |  |  |  |  | Model Number |  |  |  |  |  |  |
| Serial Number |  |  |  |  | Capacity |  |  |  |  | GPM |  |
| Volts/Phase |  |  | Function |  |  | Service Area |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |

| Boiler 2 Information |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Make |  |  |  |  | Model Number |  |  |  |  |  |  |
| Serial Number |  |  |  |  | Capacity |  |  |  |  | GPM |  |
| Volts/Phase |  |  | Function |  |  | Service Area |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |

| Associated Checklists |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Heating Hot Water Pump | ☐ | Heating Hot Water Piping | ☐ | BAS | ☐ |
| Other: | ☐ | Other: | ☐ | Other: | ☐ |
| Comments: |  |  |  |  |  |

| Requested documentation submitted | Rec’d | Comments |
| --- | --- | --- |
| Manufacturer’s cut sheets | ☐ |  |
| Performance data (pump curves, coil data, etc.) | ☐ |  |
| Installation and startup manual and plan | ☐ |  |
| O&M manuals | ☐ |  |
| Factory test results | ☐ |  |
| Sequences and control strategies | ☐ |  |
| Warranty Certificate | ☐ |  |
| Comments: |  |  |

| Installation Checks |  |  |  |
| --- | --- | --- | --- |
| Check if acceptable, provide comment if unacceptable |  | NA | Comment |
| General |  |  |  |
| General appearance good, no apparent damage | ☐ | ☐ |  |
| Installation is per manufacturer’s instructions | ☐ | ☐ |  |
| Seismic restraints in place | ☐ | ☐ |  |
| Pipe fittings and accessories complete | ☐ | ☐ |  |
| Hydronic system flushing complete and strainers cleaned | ☐ | ☐ |  |
| Test plugs (P/T) installed near all control sensors and as per spec | ☐ | ☐ |  |
| Flow switch installed as required | ☐ | ☐ |  |
| Equipment labels affixed | ☐ | ☐ |  |
| Tube pull and access door space adequate and to code | ☐ | ☐ |  |
| Combustion air supply installed | ☐ | ☐ |  |
| No leaking apparent | ☐ | ☐ |  |
| Draft Fan (if applicable) |  |  |  |
| Fan is installed per manufacturer’s instructions | ☐ | ☐ |  |
| Casing in good condition; no dents | ☐ | ☐ |  |
| Mountings checked and shipping bolts removed | ☐ | ☐ |  |
| Vibration isolators installed | ☐ | ☐ |  |
| Plenums free of debris | ☐ | ☐ |  |
| Fan rotates freely and in correct direction | ☐ | ☐ |  |
| Bearings lubricated | ☐ | ☐ |  |
| Equipment guards and safety devices installed | ☐ | ☐ |  |
| Starter installed and size coordinated with motor | ☐ | ☐ |  |
| Motor correctly aligned | ☐ | ☐ |  |
| Gas Train |  |  |  |
| Gas train Installed in accordance with NFPA, FM and IRI | ☐ | ☐ |  |
| Gas train checked for leaks | ☐ | ☐ |  |
| Gas piping installed and tested | ☐ | ☐ |  |
| Gas train vents are terminated per code | ☐ | ☐ |  |

| Installation Checks |  |  |  |
| --- | --- | --- | --- |
| Check if acceptable, provide comment if unacceptable |  | NA | Comment |
| Gas train safety devices are operational | ☐ | ☐ |  |
| Drip leg provided in gas main | ☐ | ☐ |  |
| Gas cock valve orientation per manufacturers recommendations | ☐ | ☐ |  |
| Gas cock valve accessible and travels freely | ☐ | ☐ |  |
| Gas cock checked for leaks in closed position with the other gas train valves open | ☐ | ☐ |  |
| Gas meter installed per manufacturer’s instructions | ☐ | ☐ |  |
| Gas meter properly located in non-turbulent section of pipe | ☐ | ☐ |  |
| Gas meter is properly oriented | ☐ | ☐ |  |
| Gas meter is wired correctly | ☐ | ☐ |  |
| Gas meter is accessible for test and service | ☐ | ☐ |  |
| Gas pressure adjusted and verified within acceptable range | ☐ | ☐ |  |
| Confirmed gas PRV operation | ☐ | ☐ |  |
| Gas pressure sensor limits are appropriate for application | ☐ | ☐ |  |
| Hi gas pressure switch installed per manufacturer’s instructions | ☐ | ☐ |  |
| Hi gas pressure switch is properly wired | ☐ | ☐ |  |
| Low gas pressure switch installed per manufacturer’s instructions | ☐ | ☐ |  |
| Low gas pressure switch is properly wired | ☐ | ☐ |  |
| Gas control valve installed per manufacturer’s instructions | ☐ | ☐ |  |
| Gas control valve installed vertical with direction of flow confirmed | ☐ | ☐ |  |
| Gas control valve accessible and travels freely | ☐ | ☐ |  |
| Gas control valve checked for leaks in closed position with the other gas train valves open | ☐ | ☐ |  |
| Gas control valve had no visible damage | ☐ | ☐ |  |
| Gas control valve nameplate readings checked against application and is applied correctly | ☐ | ☐ |  |
| Drum relief valve setting adequate for application | ☐ | ☐ |  |
| Drum relief valve discharge properly piped | ☐ | ☐ |  |
| Stop-Check valve pressure rating applicable for duty | ☐ | ☐ |  |
| Stop-Check valve installed per manufacturers instructions | ☐ | ☐ |  |
|  |  | ☐ |  |
| Piping |  |  |  |
| Hydronic piping complete, including blowdown system, makeup water piping and safety reliefs | ☐ | ☐ |  |
| Piping supported independently of the Boiler | ☐ | ☐ |  |
| Hydronic system flushing complete and strainers cleaned | ☐ | ☐ |  |
| Isolation valves and balancing valves installed | ☐ | ☐ |  |
| Piping type and flow direction labeled on piping | ☐ | ☐ |  |

| Installation Checks |  |  |  |
| --- | --- | --- | --- |
| Check if acceptable, provide comment if unacceptable |  | NA | Comment |
| Chemical treatment system or plan installed | ☐ | ☐ |  |
| Unions installed to allow for easy removal of control valves | ☐ | ☐ |  |
| Electrical and Controls |  |  |  |
| Power disconnect is located within site of the unit it controls and labeled | ☐ | ☐ |  |
| All electric connections tight | ☐ | ☐ |  |
| Grounding installed for components and unit | ☐ | ☐ |  |
| Safeties installed and operational | ☐ | ☐ |  |
| Starter overload breakers installed and correct size | ☐ | ☐ |  |
| All control devices and wiring complete | ☐ | ☐ |  |
| Control system interlocks connected and functional | ☐ | ☐ |  |
| Smoke detectors in place | ☐ | ☐ |  |
| Multiple boiler interlocks completed | ☐ | ☐ |  |
| Flue |  |  |  |
| Installed per manufacturers instructions | ☐ | ☐ |  |
| Sloped toward boiler | ☐ | ☐ |  |
| Clearance to combustibles per code | ☐ | ☐ |  |
| Protection in place to prevent burning hazard | ☐ | ☐ |  |
| Discharge is protected from rain and blockage | ☐ | ☐ |  |
| Provisions in place for expansion compensation | ☐ | ☐ |  |
| Discharge is located to preclude re-entrainment back into the building | ☐ | ☐ |  |
| Draft checked and meets minimum requirements of boiler manufacturer | ☐ | ☐ |  |
| Low Water Cutoff |  |  |  |
| Installed per manufacturer’s instructions | ☐ | ☐ |  |
| Wire terminations checked and correct | ☐ | ☐ |  |
|  | ☐ | ☐ |  |
| Sensors and Gages |  |  |  |
| Temperature, pressure and flow gages and sensors installed | ☐ | ☐ |  |
| Piping gages, BAS and associated panel temperature and pressure readouts match. | ☐ | ☐ |  |
| TAB |  |  |  |

| Installation Checks |  |  |  |
| --- | --- | --- | --- |
| Check if acceptable, provide comment if unacceptable |  | NA | Comment |
| Installation of system and balancing devices allowed balancing to be completed following specified NEBB or AABC procedures and contract documents | ☐ | ☐ |  |

| Operational Checks |  |  |  |
| --- | --- | --- | --- |
| Check if acceptable, provide comment if unacceptable |  | NA | Comments |
| Measure line to line voltage phase imbalance for all three-phase motors: (%Imbalance = 100 x (avg. - lowest) / avg.) Record imbalance of compressor. Imbalance less than 2%? | ☐ | ☐ |  |
| Record full load running amps for all three-phase motors: rated FL amps x srvc factor = (Max amps). Running less than max? | ☐ | ☐ |  |
| No unusual noise and vibration when running | ☐ | ☐ |  |
| Boiler safeties energized and tested | ☐ ☐ | ☐ |  |
| Specified sequences of operation and operating schedules have been implemented with all variations documented | ☐ | ☐ |  |
| Specified point-to-point checks have been completed and documentation record submitted for this system | ☐ | ☐ |  |
| Startup report completed with this checklist attached. (Includes full listing of all internal settings with notes as to which settings are BAS controlled or monitored and which are integral.) | ☐ | ☐ |  |
| Startup report includes written certification from boiler manufacturer that all specified features, controls and safeties have been installed and are functioning properly and that the installation and application comply with the manufacturer’s recommendations. | ☐ | ☐ |  |
| Startup report includes optimal and actual percent CO2, CO, O2, stack temperature; combustion efficiency | ☐ ☐ | ☐ ☐ |  |
| Piping gages, BAS and boiler temperature and pressure readouts match (see calibration section below) | ☐ | ☐ |  |

# Sensor and Actuator Calibration

All field-installed sensors and gages, and all actuators (dampers and valves) on this piece of equipment shall be calibrated in accordance with Specification Section 01810. All test instruments shall have had a certified calibration within the last 12 months: Y/N	. Sensors installed in the unit at the factory with calibration certification provided need not be field calibrated.

| Sensor or Actuator Tag & Location | Location OK | 1st Gage or BAS Value | Instrument Measured Value | Final Gage or BAS Value | Pass Y / N |
| --- | --- | --- | --- | --- | --- |

Comments:

| Sensor or Actuator Tag & Location | Location OK | 1st Gage or BAS Value | Instrument Measured Value | Final Gage or BAS Value | Pass Y / N |
| --- | --- | --- | --- | --- | --- |

*Fill out all form fields before signing!

Name		 	Organization			Title			Signature 
 
_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________
 
_________________________________________________________________________________________________________________

_________________University of Missouri Commissioning Authority