# Cooling Tower Construction Checklist

| Project: |  |
| --- | --- |

| Date: |  |
| --- | --- |
| Cooling Tower Tag: |  |
| Building: |  |
| Location: |  |

# Submittal / Approvals

Submittal. The above equipment and systems integral to them are complete and ready for functional testing. The checklist items are complete and have been checked off only by parties having direct  knowledge of the event, as marked below, respective to each responsible contractor. This construction checklist is submitted for approval, subject to an attached list of outstanding items yet to be completed. A Statement of Correction will be submitted upon completion of any outstanding areas. None of the outstanding items preclude safe and reliable functional tests being performed.		 List attached.

| Mechanical Contractor | Date | Controls Contractor | Date |
| --- | --- | --- | --- |
| Electrical Contractor | Date | Sheet Metal Contractor | Date |
| TAB Contractor | Date | General Contractor | Date |

Construction checklist items are to be completed as part of startup and initial checkout, preparatory to functional testing.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- If this form is not used for documenting, one of similar rigor shall be used.

- Contractors assigned responsibility for sections of the checklist shall be responsible to see that checklist items by their subcontractors are completed and checked off.

Approvals. This filled-out checklist has been reviewed. Its completion is approved with the exceptions noted below.

| Commissioning Authority | Date | Owner’s Representative | Date |
| --- | --- | --- | --- |

| Tower 1 Information |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Make |  |  |  |  | Model Number |  |  |  |  |  |  |
| Serial Number |  |  |  |  | Capacity |  |  |  |  | GPM |  |
| Volts/Phase |  |  | Function |  |  | Service Area |  |  |  |  |  |
| Motor Hp |  |  | Motor Eff |  |  | RPM |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |

| Tower 2 Information |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Make |  |  |  |  | Model Number |  |  |  |  |  |  |
| Serial Number |  |  |  |  | Capacity |  |  |  |  | GPM |  |
| Volts/Phase |  |  | Function |  |  | Service Area |  |  |  |  |  |
| Motor Hp |  |  | Motor Eff |  |  | RPM |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |

| Associated Checklists |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Condenser Water Pump | ☐ | Heat Exchanger | ☐ | BAS | ☐ |
| Condenser Water Piping | ☐ | Chiller | ☐ |  |  |
| Comments: |  |  |  |  |  |

| Requested documentation submitted | Rec’d | Comments |
| --- | --- | --- |
| Manufacturer’s cut sheets | ☐ |  |
| Performance data (pump curves, coil data, etc.) | ☐ ☐ |  |
| Installation and startup manual and plan | ☐ ☐ |  |
| O&M manuals | ☐ |  |
| Factory test results | ☐ |  |
| Sequences and control strategies | ☐ |  |
| Warranty Certificate | ☐ |  |
| Comments: |  |  |

| Installation Checks |  |  |  |
| --- | --- | --- | --- |
| Check if Acceptable; Provide comment if unacceptable |  | NA | Comment |
| General |  |  |  |
| General appearance good, no apparent damage | ☐ | ☐ |  |
| Tower foundation is installed per structural drawings | ☐ | ☐ |  |
| Seismic anchoring (holdown bolts) installed per structural drawings | ☐ | ☐ |  |
| Platforms, Ladders and Handrails installed per OSHA | ☐ | ☐ |  |
| Manufacturer's required maintenance clearance provided | ☐ | ☐ |  |
| Tower fill installed per manufacturers instructions | ☐ | ☐ |  |
| Spray nozzles clean | ☐ | ☐ |  |
| Distribution headers balanced | ☐ | ☐ |  |
| Outlet screens clean | ☐ | ☐ |  |
| Basin clean and clear of any debris | ☐ | ☐ |  |
| Condenser Water system fill complete | ☐ | ☐ |  |
| Condenser Water chemical treatment installed and functional | ☐ | ☐ |  |
| Condenser Water filtration system installed and functional | ☐ | ☐ |  |
| Condenser Water makeup water piping installed and functional | ☐ | ☐ |  |
| Permanent labels affixed | ☐ | ☐ |  |
| Vibration isolation installed if applicable | ☐ | ☐ |  |
| Piping |  |  |  |
| Tower piping installation checked against the drawings and all devices gages and appurtenances are in place | ☐ | ☐ |  |
| Piping supported independently of the tower | ☐ | ☐ |  |
| Piping type and flow direction labeled on piping | ☐ | ☐ |  |
| Isolation valves and piping specialties installed | ☐ | ☐ |  |
| Equalizer line installed and properly supported | ☐ | ☐ |  |
| Overflow and drain is functional and piped to a proper discharge receptor | ☐ | ☐ |  |
| Venting in place as required | ☐ | ☐ |  |
| Condenser system flushing complete and strainers cleaned | ☐ | ☐ |  |
| Fan |  |  |  |
| Fan lubricated | ☐ | ☐ |  |
| Fan drive properly aligned | ☐ | ☐ |  |
| Fan turns freely, fan wheel is balanced | ☐ | ☐ |  |
| Fan and Motor rotation checked | ☐ | ☐ |  |
| Fan guard or shield is properly installed | ☐ | ☐ |  |

| Vibration isolation devices installed and functional | ☐ | ☐ |  |
| --- | --- | --- | --- |
| Vibration sensor is installed and wired if applicable | ☐ | ☐ |  |
| Electrical and Controls |  |  |  |
| Power disconnects located within site of the unit it controls and labeled | ☐ | ☐ |  |
| All electric connections tight | ☐ | ☐ |  |
| Grounding installed for components and unit | ☐ | ☐ |  |
| Safeties installed and operational | ☐ | ☐ |  |
| Starter overload breakers installed and correct size | ☐ | ☐ |  |
| All control devices and wiring complete | ☐ | ☐ |  |
| Control system interlocks connected and functional | ☐ | ☐ |  |
| Size of overcurrent heater in motor starter correct (where applicable) | ☐ | ☐ |  |
| HOA Switch installed per manufacturer’s instructions (if applicable) | ☐ | ☐ |  |
| Operation of HOA switch checked in all positions | ☐ | ☐ |  |
| Proper safeties in control when HOA switch in Hand position | ☐ | ☐ |  |
| VFD |  |  |  |
| Installation per manufacturer's requirements and start up instructions completed | ☐ | ☐ |  |
| Drive location not subject to excessive moisture or dirt | ☐ | ☐ |  |
| Drive location not subject to excessive temperatures | ☐ | ☐ |  |
| Appropriate Volts vs. Hz curve is being used | ☐ | ☐ |  |
| Drive size matches motor size | ☐ | ☐ |  |
| Drive mounted on house keeping pad (if applicable) | ☐ | ☐ |  |
| Cooling air flow path clean and unobstructed | ☐ | ☐ |  |
| Permanent label affixed and UL stamp approved | ☐ | ☐ |  |
| VFD interlocked to control system | ☐ | ☐ |  |
| Unit is programmed with full written programming record on site | ☐ | ☐ |  |
| Accel time set to and Decel time set to | ☐ | ☐ |  |
| Operation checked in HAND, OFF, and AUTO. As applicable operation also checked in BYPASS | ☐ | ☐ |  |
| Where applicable, ensure safeties are active in all modes | ☐ | ☐ |  |
| Coordinated with BAS for all interface ranges and signal isolation | ☐ | ☐ |  |
| Restart on Power Failure parameter set to auto | ☐ | ☐ |  |
| VFD powered (wired to controlled equipment) | ☐ | ☐ |  |
| Grounding installed for components and unit | ☐ | ☐ |  |
| Drive min and max speed set to Hz min and 60 Hz max | ☐ | ☐ |  |
| Security settings set per Owner direction and Password documented for Owner | ☐ | ☐ |  |
| Drive response to loss of signal set to | ☐ | ☐ |  |

| Output pulse resolution set to MHz. (This is coordinated with the application to minimize audible noise and coordinated with driven bearing allowances.) | ☐ | ☐ |  |
| --- | --- | --- | --- |
| Checked the input voltage with drive disconnected | ☐ | ☐ |  |
| Input of motor FLA represents 100% to 105% of motor FLA rating | ☐ | ☐ |  |
| Upper frequency limit set at 100%, unless explained otherwise | ☐ | ☐ |  |
| Sensors and Gages |  |  |  |
| Temperature, pressure and flow gages and sensors installed | ☐ | ☐ |  |
| Piping gages, BAS and associated panel temperature and pressure readouts match | ☐ | ☐ |  |
| TAB |  |  |  |
| Installation of system and balancing devices allowed balancing to be completed following specified NEBB or AABC procedures and contract documents | ☐ | ☐ |  |

| Operational Checks |  |  |  |
| --- | --- | --- | --- |
| Check if Acceptable; Provide comment if unacceptable |  | NA | Comment |
| Specified sequences of operation and operating schedules have been provided with all variations documented | ☐ | ☐ |  |
| Specified point-to-point checks have been completed and documentation record submitted for this system | ☐ | ☐ |  |
| Startup report completed with this checklist attached (includes full listing of all internal settings with notes as to which settings are BAS controlled or monitored and which are integral | ☐ | ☐ |  |
| Startup report includes written certification from cooling tower manufacturer that all specified features, controls and safeties have been installed and are functioning properly and that the installation and application comply with the manufacturer’s recommendations | ☐ | ☐ |  |
| Start up complete | ☐ | ☐ |  |

# Sensor and Actuator Calibration

All field-installed sensors and gages, and all actuators (dampers and valves) on this piece of equipment shall be calibrated in accordance with Specification Section 01810. All test instruments shall have had a certified calibration within the last 12 months: Y/N	. Sensors installed in the unit at the factory with calibration certification provided need not be field calibrated.

| Sensor or Actuator Tag & Location | Location OK | 1st Gage or BAS Value | Instrument Measured Value | Final Gage or BAS Value | Pass Y / N |
| --- | --- | --- | --- | --- | --- |

| Sensor or Actuator Tag & Location | Location OK | 1st Gage or BAS Value | Instrument Measured Value | Final Gage or BAS Value | Pass Y / N |
| --- | --- | --- | --- | --- | --- |

Comments:

*Fill out all form fields before signing!

Name		 	Organization			Title			Signature 
 
_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________
 
_________________________________________________________________________________________________________________

_________________University of Missouri Commissioning Authority