# Domestic Water Booster Pump Test Procedure

| Project: |  |
| --- | --- |

| Date: |  |
| --- | --- |
| Pump Tag: |  |
| Building: |  |
| Location: |  |

| First Test Date | Re-Test Date | Reason for Re-Test | Seasonal Test Required |
| --- | --- | --- | --- |

Conditions of Testing

| Ambient Conditions |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| DB |  | WB |  | RH |  |
| Bar Press |  | Wind Speed |  | Wind Dir |  |

| Occupancy Schedule |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| M-F |  | Saturday |  | Sunday |  | Holiday |  |

| Setpoints | Design | Actual |
| --- | --- | --- |
| Temperature Sensor |  |  |
| Static Pressure Sensor |  |  |

Describe Overrides / Status and Operating Condition of Equipment:

Test Participants

| Manufacturers: |  |
| --- | --- |
| Contractors: |  |
| Building Owner / Representatives: |  |
| Commissioning Specialists: |  |

Test Instruments

| Instrumentation |  |  |  |  |
| --- | --- | --- | --- | --- |
| Manufacturer/Model | Serial Number | Range | Accuracy/Resolution | Last Calibration Date |

Approvals. This filled-out test procedure has been reviewed. Its completion is approved with the exceptions noted below.

| Mechanical Contractor | Date | Controls Contractor | Date |
| --- | --- | --- | --- |
| Electrical Contractor | Date | Sheet Metal Contractor | Date |
| TAB Contractor | Date | General Contractor | Date |
| Commissioning Authority | Date | Owner’s Representative | Date |

System Description

Domestic Water Booster Pump Sequence of Operation:

(Insert Sequence of Operation here)

Sensor Calibration Verification

Check the sensors listed below for calibration and adequate location. All field-installed sensors and gages, and all actuators (dampers and valves) on this piece of equipment shall be calibrated in accordance with Specification Section 01810. All test instruments shall have had a certified calibration within the last 12 months: Y/N	. Sensors installed in the unit at the factory with calibration certification provided need not be field calibrated.

| Sensor | Location OK | 1st Gage or BAS Value | Instrument Measured Value | Final Gage or BAS Value | Pass Y / N |
| --- | --- | --- | --- | --- | --- |

Device Calibration Verification

All field-installed sensors and gages, and all actuators (dampers and valves) on this piece of equipment shall be calibrated in accordance with Specification Section 01810. All test instruments shall have had a certified calibration within the last 12 months: Y/N	. Devices installed in the unit at the factory with calibration certification provided need not be field calibrated.

| Device or Actuator Tag & Location | Procedure / State | 1st BAS Value | Site Observation | Final BAS Value | Pass Y / N |
| --- | --- | --- | --- | --- | --- |

Load Verification Testing

| Load Parameter | Design | Actual | Comments |
| --- | --- | --- | --- |
| GPM |  |  |  |
| Pressure |  |  |  |
| RPM |  |  |  |
| Voltage |  |  |  |
| Amperage |  |  |  |

Functional Testing Record General

| Function / Mode | Test Method: Manual, Automatic, Either or Both | Require d Seasona l Test Y or N |
| --- | --- | --- |
| 1. Test each sequence in the sequence of operations, and other significant modes and sequences not mentioned; including startup, shutdown, unoccupied & manual modes and power failure. Test functionality of this piece of equipment or system in all control strategies or interlocks that it is associated with. | Manual |  |
| 2. Verify schedules and setpoints to be reasonable and appropriate | Review |  |
| 3. Speed controls | Both |  |
| 4. Sensor calibration checks on any controlling temperature or pressure sensor | Manual |  |

Test Procedure

| Test Procedure | Expected Response | P | F | Comments | Req’d Retest |
| --- | --- | --- | --- | --- | --- |

| Test Procedure | Expected Response | P | F | Comments | Req’d Retest |
| --- | --- | --- | --- | --- | --- |
| Standby check. HOA in Auto position. Unit commanded Off by BAS | Verify by visual inspection that: - Pump is off. |  |  |  |  |
| HOA in Auto position. Unit commanded On by BAS. | Verify by visual inspection that: - System maintaining pressure setpoint. - Pump may be on. |  |  |  |  |
| With units running at low flow condition, open valves to increase flow. | Verify by visual inspection that: - System maintaining pressure setpoint. - Record pressure: psig - Lag pump stages On. |  |  |  |  |
| Record full load running amps for each pump. rated FL amps x srvc factor = (Max amps). Running less than max? | Pump runs within design parameters. Record FLA: A |  |  |  |  |
| With unit running at high flow condition, close valves to decrease flow. | Verify by visual inspection that: - System maintaining pressure setpoint. - Record pressure: psig - Lag pump stages Off. |  |  |  |  |
| With unit running at low flow, close all valves until unit stops. Once unit stops, open valve for very low flow. | Verify by visual inspection that: - Hydrostatic tank maintaining pressure setpoint. |  |  |  |  |

| Test Procedure | Expected Response | P | F | Comments | Req’d Retest |
| --- | --- | --- | --- | --- | --- |
| Verification of safeties and alarms. | Record setpoints and time delays: - Low suction pressure alarm (x second delay) - Low suction pressure shutdown - Low system pressure alarm (30 second delay) - High system pressure alarm - High system pressure shutdown - Pump failure - BAS failure contacts |  |  |  |  |

Required Monitoring

All points listed below shall be trended by the BAS for the period indicated.

| Point | Trend Interval (min.) | Minimum Time Period of Trend | Hard Copy? (Y/N) | ASCII File? (Y/N) |
| --- | --- | --- | --- | --- |
| Pressure |  |  |  |  |
| Pump status |  |  |  |  |
| Alarm |  |  |  |  |

Remarks:

Acceptance Criteria (referenced by function or mode ID)

For the conditions, sequences and modes tested, the fans, integral components and related equipment respond to changing conditions and parameters appropriately as expected, as specified and according to acceptable operating practice.

Comments with Acceptance Criteria:

*Fill out all form fields before signing!

Name		 	Organization			Title			Signature 
 
_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________
 
_________________________________________________________________________________________________________________

_________________University of Missouri Commissioning Authority