# Panel Construction Checklist

| Project: |  |
| --- | --- |

| Date: |  |
| --- | --- |
| Building: |  |
| Location: |  |

# Submittal / Approvals

Submittal. The above equipment and systems integral to them are complete and ready for functional testing. The checklist items are complete and have been checked off only by parties having direct knowledge of the event, as marked below, respective to each responsible contractor. This construction checklist is submitted for approval, subject to an attached list of outstanding items yet to be completed. A Statement of Correction will be submitted upon completion of any outstanding areas. None of the outstanding items preclude safe and reliable functional tests being performed.		 List attached.

| Electrical Contractor | Date | General Contractor | Date |
| --- | --- | --- | --- |

Construction checklist items are to be completed as part of startup & initial checkout, preparatory to performing test procedures.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- If this form is not used for documenting, one of similar rigor shall be used.

- Contractors assigned responsibility for sections of the checklist shall be responsible to see that checklist items by their subcontractors are completed and checked off.

Approvals. This filled-out checklist has been reviewed. Its completion is approved with the exceptions noted below.

| Commissioning Authority | Date | Owner’s Representative | Date |
| --- | --- | --- | --- |

Panel Schedule (Add as required)

| Panel Information |  |  |  |
| --- | --- | --- | --- |
| Panel Tag |  | Panel Location |  |
| System (Circle one) | Power or Lighting | 208-120 or 480-277 | Normal or Emergency |
| Manufacturer |  | Model Number |  |
| Serial Number |  | Short Circuit Capacity |  |
| Volts/Phase Rating |  | Amperage Rating |  |
| Service Area |  |  |  |
| Comments: |  |  |  |

| Associated Checklists |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Grounding |  | Lighting |  | Low Voltage Transformer |  |
| Low Voltage MCC |  | Low Voltage Switchgear |  | Unit Substation |  |
| Unit Substation Transformer |  | Other |  | Other |  |
| Comments: |  |  |  |  |  |

| Requested documentation submitted | Rec’d | Comments |
| --- | --- | --- |
| Manufacturer’s cut sheets |  |  |
| Installation and startup manual and plan |  |  |
| O&M manuals |  |  |
| Sequences and control strategies |  |  |
| Warranty Certificate |  |  |
| Comments: |  |  |

| Distribution Panel Enclosure/Cabinetry |  |  |  |
| --- | --- | --- | --- |
| Check if Acceptable; Provide comment if unacceptable |  | NA | Comment |
| Equipment installed per manufacturer’s instructions and specifications |  |  |  |

| Equipment installed agrees with shop drawings and specifications |  |  |  |
| --- | --- | --- | --- |
| Verify mounting, location and clearances are per plans and specifications |  |  |  |
| Inspect for physical, electrical and mechanical condition of equipment and cabinet - no damage evident |  |  |  |
| Inspect panels and doors for proper fit and alignment |  |  |  |
| Equipment labels permanently affixed |  |  |  |
| Panel is clean and clear of dust or dirt |  |  |  |
| Verify the application of manufacturer recommended torque values applied to bolted connections |  |  |  |
| Verify correct circuit breaker sizes and types per the specifications and manufacturer’s drawings |  |  |  |
| Inspect insulators, barriers and shields for damage or contamination |  |  |  |
| Verify that ground bus is properly bonded to enclosure, enclosure is grounded and resistance to ground meets grounding specifications. |  |  |  |
| Neutral bus isolated from cabinet |  |  |  |
| Megger test of bus – phase to phase and phase to ground. Test voltage per manufacturer’s recommendations. |  |  |  |
| Circuit Breakers 208/120 VAC Panels |  |  |  |
| Installed per manufacturer’s instructions, plans and specifications |  |  |  |
| No physical damage |  |  |  |
| Verify voltage and current rating of circuit breaker are per plans and specifications |  |  |  |
| Verify breakers are mounted securely and operates smoothly |  |  |  |
| Verify wire is properly installed and suitable size for breaker |  |  |  |
| Check cell fit and element alignment |  |  |  |
| Check racking mechanism |  |  |  |

| Operational Checks |  |  |  |
| --- | --- | --- | --- |
| Check if Acceptable; Provide comment if unacceptable |  | NA | Comment |
| Specified sequences of operation and operating schedules have been provided with all variations documented |  |  |  |
| Specified point-to-point checks have been completed and documentation record submitted for this system |  |  |  |

Comments:

*Fill out all form fields before signing!

Name		 	Organization			Title			Signature 
 
_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________
 
_________________________________________________________________________________________________________________

_________________University of Missouri Commissioning Authority