# Exhaust Fan Construction Checklist

| Project: |  |
| --- | --- |

| Date: |  |
| --- | --- |
| Building: |  |
| Location: |  |

# Submittal / Approvals

Submittal. The above equipment and systems integral to them are complete and ready for functional testing. The checklist items are complete and have been checked off only by parties having direct knowledge of the event, as marked below, respective to each responsible contractor. This construction checklist is submitted for approval, subject to an attached list of outstanding items yet to be completed. A Statement of Correction will be submitted upon completion of any outstanding areas. None of the outstanding items preclude safe and reliable functional tests being performed. 	 List attached.

| Mechanical Contractor | Date | Controls Contractor | Date |
| --- | --- | --- | --- |
| Electrical Contractor | Date | Sheet Metal Contractor | Date |
| TAB Contractor | Date | General Contractor | Date |

Construction checklist items are to be completed as part of startup & initial checkout, preparatory to performing test procedures.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- If this form is not used for documenting, one of similar rigor shall be used.

- Contractors assigned responsibility for sections of the checklist shall be responsible to see that checklist items by their subcontractors are completed and checked off.

Approvals. This filled-out checklist has been reviewed. Its completion is approved with the exceptions noted below.

| Commissioning Authority | Date | Owner’s Representative | Date |
| --- | --- | --- | --- |

| Exhaust Fan Information |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Make |  |  |  |  | Model Number |  |  |  |  |  |
| Serial Number |  |  |  |  | Capacity CFM min |  |  |  | CFM max |  |
| Total Air PD (In WC) |  |  |  |  | Sound Power Level @ 63, 250, & 1KHz |  |  |  |  |  |
| Volts/Phase |  |  | Function |  |  | Service Area |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |

| Associated Checklists |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| AHU | ☐ | Ductwork | ☐ | BAS | ☐ |
| Other | ☐ | Other | ☐ | Other | ☐ |
| Comments: |  |  |  |  |  |

| Requested documentation submitted | Rec’d | Comments |
| --- | --- | --- |
| Manufacturer’s cut sheets | ☐ |  |
| Performance data (pump curves, coil data, etc.) | ☐ |  |
| Installation and startup manual and plan | ☐ |  |
| O&M manuals | ☐ |  |
| Factory test results | ☐ |  |
| Sequences and control strategies | ☐ |  |
| Warranty Certificate | ☐ |  |
| Comments: |  |  |

| Installation Checks |  |  |  |
| --- | --- | --- | --- |
| Check if acceptable, provide comment if unacceptable |  | NA | Comment |
| General |  |  |  |
| Cabinet and general installation | ☐ | ☐ |  |
| Permanent labels affixed | ☐ | ☐ |  |
| Casing condition good: no dents, leaks, door gaskets installed | ☐ | ☐ |  |
| Access doors close tightly – no leaks | ☐ | ☐ |  |
| Mountings checked and shipping bolts removed | ☐ | ☐ |  |
| Connection between duct and unit tight and in good condition | ☐ | ☐ |  |
| Vibration isolation equipment installed & released from shipping locks | ☐ | ☐ |  |
| Maintenance access acceptable | ☐ | ☐ |  |
| Sound attenuation installed | ☐ | ☐ |  |
| Thermal insulation properly installed and according to specification | ☐ | ☐ |  |
| Instrumentation installed according to specification (thermometers, pressure gages, flow meters, etc.) | ☐ | ☐ |  |
| Clean up of equipment completed per contract documents | ☐ | ☐ |  |
| Filters installed and replacement type and efficiency permanently affixed to housing--construction filters removed | ☐ | ☐ |  |
| Fans and Dampers |  |  |  |
| Exhaust fan and motor aligned | ☐ | ☐ |  |
| Exhaust fan belt tension & condition good | ☐ | ☐ |  |
| Exhaust fan protective shrouds for belts in place and secure | ☐ | ☐ |  |
| Exhaust fan area clean | ☐ | ☐ |  |
| Exhaust fan and motor lube lines installed and lubed | ☐ | ☐ |  |
| Filters clean and tight fitting | ☐ | ☐ |  |
| Filter pressure differential measuring device installed and functional (magnahelic, inclined manometer, etc.) | ☐ | ☐ |  |
| Smoke and fire dampers installed properly per contract docs (proper location, access doors, appropriate ratings verified) | ☐ | ☐ |  |
| All dampers close tightly | ☐ | ☐ |  |
| All damper actuators installed | ☐ | ☐ |  |
| Ducts |  |  |  |
| Sound attenuators installed | ☐ | ☐ |  |
| Duct joint sealant properly installed | ☐ | ☐ |  |
| No apparent severe duct restrictions | ☐ | ☐ |  |
| Turning vanes in square elbows as per drawings | ☐ | ☐ |  |
| Pressure leakage tests completed | ☐ | ☐ |  |

| Installation Checks |  |  |  |
| --- | --- | --- | --- |
| Check if acceptable, provide comment if unacceptable |  | NA | Comment |
| Branch duct control dampers operable | ☐ | ☐ |  |
| Ducts cleaned as per specifications | ☐ | ☐ |  |
| Balancing dampers installed as per drawings and TAB’s site visit | ☐ | ☐ |  |
| Electrical and Controls |  |  |  |
| Power disconnects located within site of the unit it controls and labeled | ☐ | ☐ |  |
| All electric connections tight | ☐ | ☐ |  |
| Grounding installed for components and unit | ☐ | ☐ |  |
| Safeties installed and operational | ☐ | ☐ |  |
| Starter overload breakers installed and correct size | ☐ | ☐ |  |
| All control devices and wiring complete | ☐ | ☐ |  |
| Control system interlocks connected and functional | ☐ | ☐ |  |
| Smoke detectors in place | ☐ | ☐ |  |
| VFD |  |  |  |
| Installation per manufacturer's requirements and start up instructions completed | ☐ | ☐ |  |
| Drive location not subject to excessive moisture or dirt | ☐ | ☐ |  |
| Drive location not subject to excessive temperatures | ☐ | ☐ |  |
| Appropriate Volts vs. Hz curve is being used | ☐ | ☐ |  |
| Drive size matches motor size | ☐ | ☐ |  |
| Drive mounted on house keeping pad (if applicable) | ☐ | ☐ |  |
| Cooling air flow path clean and unobstructed | ☐ | ☐ |  |
| Permanent label affixed and UL stamp approved | ☐ | ☐ |  |
| VFD interlocked to control system | ☐ | ☐ |  |
| Unit is programmed with full written programming record on site | ☐ | ☐ |  |
| Accel time set to and Decel time set to | ☐ | ☐ |  |
| Operation checked in HAND, OFF, and AUTO. As applicable operation also checked in BYPASS | ☐ | ☐ |  |
| Where applicable, ensure safeties are active in all modes | ☐ | ☐ |  |
| Coordinated with BAS for all interface ranges and signal isolation | ☐ | ☐ |  |
| Restart on Power Failure parameter set to auto | ☐ | ☐ |  |
| VFD powered (wired to controlled equipment) | ☐ | ☐ |  |
| Grounding installed for components and unit | ☐ | ☐ |  |
| Drive min and max speed set to Hz min and 60 Hz max | ☐ | ☐ |  |
| Security settings set per Owner direction and Password documented for Owner | ☐ | ☐ |  |

| Installation Checks |  |  |  |
| --- | --- | --- | --- |
| Check if acceptable, provide comment if unacceptable |  | NA | Comment |
| Drive response to loss of signal set to | ☐ | ☐ |  |
| Output pulse resolution set to MHz. (This is coordinated with the application to minimize audible noise and coordinated with driven bearing allowances.) | ☐ | ☐ |  |
| Checked the input voltage with drive disconnected | ☐ | ☐ |  |
| Input of motor FLA represents 100% to 105% of motor FLA rating | ☐ | ☐ |  |
| Upper frequency limit set at 100%, unless explained otherwise | ☐ | ☐ |  |
| Sensors and Gages |  |  |  |
| Temperature, pressure and flow gages and sensors installed | ☐ | ☐ |  |
| Piping gages, BAS and associated panel temperature and pressure readouts match. | ☐ | ☐ |  |
| TAB |  |  |  |
| Installation of system and balancing devices allowed balancing to be completed following specified NEBB or AABC procedures and contract documents | ☐ | ☐ |  |

| Operational Checks |  |  |  |
| --- | --- | --- | --- |
| Check if acceptable, provide comment if unacceptable |  | NA | Comments |
| Fan rotation correct (If VFD, check rotation in bypass and VFD Inverter mode) | ☐ | ☐ |  |
| Fan has no unusual noise or vibration | ☐ | ☐ |  |
| All dampers (OSA, RA, EA, etc.) stroke fully without binding and spans calibrated and BAS reading site verified | ☐ | ☐ |  |
| Specified point-to-point checks have been completed and documentation record submitted for this system | ☐ ☐ | ☐ |  |

# Sensor and Actuator Calibration

All field-installed sensors and gages, and all actuators (dampers and valves) on this piece of equipment shall be calibrated in accordance with Specification Section 01810. All test instruments shall have had a certified calibration within the last 12 months: Y/N	. Sensors installed in the unit at the factory with calibration certification provided need not be field calibrated.

| Sensor or Actuator Tag & Location | Location OK | 1st Gage or BAS Value | Instrument Measured Value | Final Gage or BAS Value | Pass Y / N |
| --- | --- | --- | --- | --- | --- |

| Sensor or Actuator Tag & Location | Location OK | 1st Gage or BAS Value | Instrument Measured Value | Final Gage or BAS Value | Pass Y / N |
| --- | --- | --- | --- | --- | --- |

Comments:

*Fill out all form fields before signing!

Name		 	Organization			Title			Signature 
 
_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________
 
_________________________________________________________________________________________________________________

_________________University of Missouri Commissioning Authority