# Project:	Date:

| FIRE ALARM SYSTEM - PRETEST CHECKLIST |  |  |  |
| --- | --- | --- | --- |
| All items below (not all inclusive) must be tested/checked/confirmed and pass prior to the final fire alarm system test. This completed form must accompany the pre-test completion certification. |  |  |  |
| Completed (place 'Y' in box below) | Date(s) | Test Party Initials | Description |
|  |  |  | CHECK AND CONFIRM ADDRESSES AND FUNCTIONS OF DETECTORS AND SOUNDERS |
|  |  |  | CHECK AND CONFIRM FUNCTION OF STROBES. ENSURE STROBES AT CORRECT LUMEN LEVEL AND SYNCHRONIZED (where applicable) |
|  |  |  | CHECK WIRING PROBLEMS AND MONITORING CAPABILITIES (GROUND AND SHORT) |
|  |  |  | CHECK SHUTDOWN OF SNAC PANELS (POWER SUPPLY PANELS). ENSURE TROUBLE AT MAIN PANEL AND AUX PANELS. |
|  |  |  | CHECK SHUTDOWN OF MAIN PANELS AND AUX PANELS. ENSURE TROUBLE AT MAIN PANEL AND AUX PANELS. |
|  |  |  | CHECK ELEVATOR RECALL FUNCTIONS AND ALTERNATE FLOOR FUNCTIONS. (Coordinate with elevator contractor-as applicable) |
|  |  |  | CHECK HEAT DETECTOR AND SMOKE DETECTOR FUNCTION AND ADDRESS. |
|  |  |  | CHECK DUCT DETECTOR FUNCTION AND ADDRESS. ENSURE SHUTDOWN OF AHU's. (Coordinate with HVAC contractor) |
|  |  |  | CHECK LABELS AND ROOM NUMBERS/NAMES - ENSURE CORRECT. |
|  |  |  | CHECK DOOR HOLDER/DOOR LOCK FUNCTIONS. ENSURE OPERATION |
|  |  |  | CHECK TIE-INS TO SPRINKLER SYSTEM. ENSURE ADDRESS AND FUNCTION. SET FLOW SWITCH DELAYS. (Coordinate with fire protection contractor) |
|  |  |  | CHECK FIRE PUMP TIE-INS. ENSURE ADDRESS AND FUNCTION. (as applicable) |
|  |  |  | TEST CONNECTION TO OFFSITE MONITORING COMPANY. CONFIRM TROUBLE AND ALARM MONITORING RECEIPT (Coordinate with Telecom) |
|  |  |  | TEST METASYS TIE-IN POINTS. CONFIRM TROUBLE AND ALARM MONITORING. (Coordinate with EMO and HVAC contractor) |
|  |  |  | PERFORM 24HR BATTERY TEST. ENSURE FIRE ALARM SOUNDS FOR 5 MINUTES AFTER 24 HOUR LOSS OF POWER. |
|  |  |  | INSURE AS-BUILT DRAWINGS ARE UPDATED AND ACCURATE AND PREPARED FOR THE FINAL TEST |
|  |  |  | Identify and list all associated equipment and systems and communicate to the GC that these items must be operational prior to the pre-test. |

*Fill out all form fields before signing!

Name		 	Organization			Title			Signature 
 
_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________
 
_________________________________________________________________________________________________________________

_________________University of Missouri Commissioning Authority