# Heating Hot Water Piping Construction Checklist

| Project: |  |
| --- | --- |

| Date: |  |
| --- | --- |
| Building: |  |
| Location: |  |

# Submittal / Approvals

Submittal. The above equipment and systems integral to them are complete and ready for functional testing. The checklist items are complete and have been checked off only by parties having direct  knowledge of the event, as marked below, respective to each responsible contractor. This construction checklist is submitted for approval, subject to an attached list of outstanding items yet to be completed. A Statement of Correction will be submitted upon completion of any outstanding areas. None of the outstanding items preclude safe and reliable functional tests being performed.		 List attached.

| Mechanical Contractor | Date | Controls Contractor | Date |
| --- | --- | --- | --- |
| Electrical Contractor | Date |  |  |
| TAB Contractor | Date | General Contractor | Date |

Construction checklist items are to be completed as part of startup & initial checkout, preparatory to performing test procedures.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- If this form is not used for documenting, one of similar rigor shall be used.

- Contractors assigned responsibility for sections of the checklist shall be responsible to see that checklist items by their subcontractors are completed and checked off.

Approvals. This filled-out checklist has been reviewed. Its completion is approved with the exceptions noted below.

| Commissioning Authority | Date | Owner’s Representative | Date |
| --- | --- | --- | --- |

| Associated Checklists |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Boiler | ☐ | Heat Exchanger | ☐ | BAS | ☐ |
| Heating Hot Water Pump(s) | ☐ | Other | ☐ | Other | ☐ |
| Comments: |  |  |  |  |  |

| Requested documentation submitted | Rec’d | Comments |
| --- | --- | --- |
| Manufacturer’s cut sheets | ☐ |  |
| Performance data (pump curves, coil data, etc.) | ☐ |  |
| Installation and startup manual and plan | ☐ |  |
| O&M manuals | ☐ |  |
| Sequences and control strategies | ☐ |  |
| Flushing and cleaning plan | ☐ |  |
| Leak test reports | ☐ |  |
| Water treatment report | ☐ |  |
| Welder Certification | ☐ |  |
| Comments: |  |  |

| Installation Checks |  |  |  |
| --- | --- | --- | --- |
| Check if acceptable, provide comment if unacceptable |  | NA | Comment |
| Piping |  |  |  |
| Piping installed per the drawings and details | ☐ | ☐ |  |
| Piping, fittings, valves and equipment properly supported and seismically anchored per the details | ☐ | ☐ |  |
| Piping, fittings and valves insulated per specification | ☐ | ☐ |  |
| In-line equipment insulated per specification | ☐ | ☐ |  |
| Piping labeled per specification with flows indicated in the correct direction | ☐ | ☐ |  |
| Strainers and low-point drains opened and verified to be clean | ☐ | ☐ |  |

| Installation Checks |  |  |  |
| --- | --- | --- | --- |
| Check if acceptable, provide comment if unacceptable |  | NA | Comment |
| Construction strainers removed | ☐ | ☐ |  |
| Test plugs (P/T) installed near all control sensors and as per spec | ☐ | ☐ |  |
| Flushing and cleaning plan submitted and approved | ☐ | ☐ |  |
| Piping system properly flushed and cleaned and temporary piping removed | ☐ | ☐ |  |
| Piping pressure tested according to contract documents | ☐ | ☐ |  |
| Chemical treatment system or plan installed | ☐ | ☐ |  |
| No leaking apparent | ☐ | ☐ |  |
| ASME pressure vessel data sheet or certification tag posted and inspection complete for each expansion tank | ☐ | ☐ |  |
| Expansion tanks verified to not be air bound and system completely full of water. System completed purged of air. | ☐ | ☐ |  |
| Air vents and bleeds at high points of systems functional | ☐ | ☐ |  |
| Provisions in place for expansion compensation | ☐ | ☐ |  |
| Record drawings updated to reflect the actual installation | ☐ | ☐ |  |
| Valves |  |  |  |
| Isolation valves provided at all branches and main takeoffs to facilitate isolation (as required by contract) | ☐ | ☐ |  |
| Valve installation per manufacturer’s instructions | ☐ | ☐ |  |
| Valve manufacturer labels permanently affixed | ☐ | ☐ |  |
| Manual isolation valves checked for proper seal and found to travel freely | ☐ | ☐ |  |
| Valves installed in proper direction |  | ☐ |  |
| Valves stroke fully and easily and spanning is calibrated (see calibration section below) | ☐ | ☐ |  |
| Valves that require a positive shut-off are verified to not be leaking when closed at normal operating pressure | ☐ | ☐ |  |
| No leaking apparent | ☐ | ☐ |  |
| Valves tagged and valve schedule submitted and displayed as required | ☐ | ☐ |  |
| Adequate maintenance clearance in provided and valve is accessible | ☐ | ☐ |  |
| Unions installed to allow for easy removal of control valves | ☐ | ☐ |  |
| Sensors and Gages |  |  |  |
| Temperature, pressure and flow gages and sensors installed | ☐ | ☐ |  |
| Piping gages, BAS and associated panel temperature and pressure readouts match. | ☐ | ☐ |  |

| Installation Checks |  |  |  |
| --- | --- | --- | --- |
| Check if acceptable, provide comment if unacceptable |  | NA | Comment |
| TAB |  |  |  |
| Installation of system and balancing devices allowed balancing to be completed following specified NEBB or AABC procedures and contract documents | ☐ | ☐ |  |

# Sensor and Actuator Calibration

All field-installed sensors and gages, and all actuators (dampers and valves) on this piece of equipment shall be calibrated in accordance with Specification Section 01810. All test instruments shall have had a certified calibration within the last 12 months: Y/N	. Sensors installed in the unit at the factory with calibration certification provided need not be field calibrated.

Comments:

| Sensor or Actuator Tag & Location | Location OK | 1st Gage or BAS Value | Instrument Measured Value | Final Gage or BAS Value | Pass Y / N |
| --- | --- | --- | --- | --- | --- |

*Fill out all form fields before signing!

Name		 	Organization			Title			Signature 
 
_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________
 
_________________________________________________________________________________________________________________

_________________University of Missouri Commissioning Authority