# Low Voltage Motor Control Center Construction Checklist

| Project: |  |
| --- | --- |

| Date: |  |
| --- | --- |
| Building: |  |
| Location: |  |

# Submittal / Approvals

Submittal. The above equipment and systems integral to them are complete and ready for functional testing. The checklist items are complete and have been checked off only by parties having direct knowledge of the event, as marked below, respective to each responsible contractor. This construction checklist is submitted for approval, subject to an attached list of outstanding items yet to be completed. A Statement of Correction will be submitted upon completion of any outstanding areas. None of the outstanding items preclude safe and reliable functional tests being performed.		 List attached.

| Electrical Contractor | Date | General Contractor | Date |
| --- | --- | --- | --- |

Construction checklist items are to be completed as part of startup & initial checkout, preparatory to performing test procedures.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- If this form is not used for documenting, one of similar rigor shall be used.

- Contractors assigned responsibility for sections of the checklist shall be responsible to see that checklist items by their subcontractors are completed and checked off.

Approvals. This filled-out checklist has been reviewed. Its completion is approved with the exceptions noted below.

| Commissioning Authority | Date | Owner’s Representative | Date |
| --- | --- | --- | --- |

| MCC Information |  |  |  |
| --- | --- | --- | --- |
| Equipment Tag |  | Location |  |
| System |  | Service Area |  |
| Manufacturer |  | Model Number |  |
| Serial Number |  | Short Circuit Capacity |  |
| Volts/Phase Rating |  | Main Bus Amperage |  |
| Other |  | Other |  |
| Comments: |  |  |  |

| Associated Checklists |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Unit Substation | ☐ | Other | ☐ | Other | ☐ |
| Comments: |  |  |  |  |  |

| Requested documentation submitted | Rec’d | Comments |
| --- | --- | --- |
| Manufacturer’s cut sheets | ☐ |  |
| Installation and startup manual and plan | ☐ |  |
| O&M manuals | ☐ |  |
| Factory test results | ☐ |  |
| Sequences and control strategies | ☐ |  |
| Warranty Certificate | ☐ |  |
| Comments: |  |  |

| MCC Enclosure/Cabinetry |  |  |  |
| --- | --- | --- | --- |
| Check if Acceptable; Provide comment if unacceptable |  | NA | Comment |
| Equipment installed per manufacturer’s instructions and specifications | ☐ | ☐ |  |
| Equipment installed agrees with shop drawings and specifications | ☐ | ☐ |  |
| Verify mounting, location and clearances are per plans and specifications | ☐ | ☐ |  |

| Inspect for physical, electrical and mechanical condition of equipment and cabinet - no damage evident | ☐ | ☐ |  |
| --- | --- | --- | --- |
| Inspect panels and doors for proper fit and alignment | ☐ | ☐ |  |
| Equipment labels permanently affixed | ☐ | ☐ |  |
| Panel is clean and clear of dust or dirt | ☐ | ☐ |  |
| Verify the application of manufacturer recommended torque values applied to bolted connections | ☐ | ☐ |  |
| Verify correct circuit breaker sizes and types per the specifications and manufacturer’s drawings | ☐ | ☐ |  |
| Seismic anchoring installed and functional where applicable (non- short circuiting) | ☐ | ☐ |  |
| Verify that all manufacturer control wiring between shipping splits is properly connected per manufacturer’s drawings and specifications | ☐ | ☐ |  |
| Inspect insulators, barriers and shields for damage or contamination | ☐ | ☐ |  |
| Verify that ground bus is properly bonded to enclosure, enclosure is grounded and resistance to ground meets grounding specifications | ☐ | ☐ |  |
| Verify three or four wire configuration | ☐ | ☐ |  |
| Neutral bus isolated from cabinet | ☐ | ☐ |  |
| Verify that bottom feed conduits align with appropriate openings in MCC and can accommodate seismic motion | ☐ | ☐ |  |
| Verify that MCC is properly grounded and resistance to ground meets grounding specifications | ☐ | ☐ |  |
| Metering (if provided) matches specified | ☐ | ☐ |  |
| Verify the vents and air inlets are free and unobstructed. Clean air filters installed (if required) | ☐ | ☐ |  |
| Megger test of bus – phase to phase and phase to ground. Test voltage per manufacturer’s recommendations | ☐ | ☐ |  |
|  | ☐ | ☐ |  |
| Main Circuit Breaker (if provided) |  |  |  |
| Installed per manufacturer’s instructions, plans and specifications | ☐ | ☐ |  |
| Verify all maintenance and service clearances are maintained | ☐ | ☐ |  |
| Verify no physical damage | ☐ | ☐ |  |
| Verify voltage and current rating of circuit breaker are per plans and specifications | ☐ | ☐ |  |
| Confirm correct application of manufacturer’s recommended lubricant | ☐ | ☐ |  |
| Verify that primary and secondary contact wipe dimensions are correct | ☐ | ☐ |  |
| Verify breakers are mounted securely and operates smoothly | ☐ | ☐ |  |
| Verify wire is properly installed and suitable size for breaker | ☐ | ☐ |  |
| Check cell fit and element alignment | ☐ | ☐ |  |
| Check racking mechanism | ☐ | ☐ |  |

| Megger test of circuit breaker – phase to phase and phase to ground. Test voltage per manufacturer’s recommendations | ☐ | ☐ |  |
| --- | --- | --- | --- |
| Inspect shutter operation | ☐ | ☐ |  |
| Verify that vacuum contact wipe dimensions are correct | ☐ | ☐ |  |
|  | ☐ | ☐ |  |
| Feeder Circuit Breakers |  |  |  |
| Installed per manufacturer’s instructions, plans and specifications | ☐ | ☐ |  |
| Verify all maintenance and service clearances are maintained | ☐ | ☐ |  |
| Verify no physical damage | ☐ | ☐ |  |
| Verify voltage and current rating of circuit breaker are per plans and specifications | ☐ | ☐ |  |
| Confirm correct application of manufacturer’s recommended lubricant | ☐ | ☐ |  |
| Verify that primary and secondary contact wipe dimensions are correct | ☐ | ☐ |  |
| Verify breakers are mounted securely and operates smoothly | ☐ | ☐ |  |
| Verify wire is properly installed and suitable size for breaker | ☐ | ☐ |  |
| Check cell fit and element alignment | ☐ | ☐ |  |
| Check racking mechanism | ☐ | ☐ |  |
| Megger test of circuit breaker – phase to phase and phase to ground. Test voltage per manufacturer’s recommendations | ☐ | ☐ |  |
| Inspect shutter operation | ☐ | ☐ |  |
| Verify that vacuum contact wipe dimensions are correct | ☐ | ☐ |  |
| Motor Starters |  |  |  |
| Installed per manufacturer’s instructions, plans and specifications | ☐ | ☐ |  |
| Verify voltage and current rating of Motor Circuit Protectors (MCP’s) are per plans and specifications | ☐ | ☐ |  |
| Verify motor starter sizes (NEMA) are per plans and specifications | ☐ | ☐ |  |

| Operational Checks |  |  |  |
| --- | --- | --- | --- |
| Check if Acceptable; Provide comment if unacceptable |  | NA | Comment |
| Verify proper phasing (A, B, C) | ☐ | ☐ |  |
| Specified sequences of operation and operating schedules have been provided with all variations documented | ☐ | ☐ |  |
| Specified point-to-point checks have been completed and documentation record submitted for this system | ☐ | ☐ |  |

Comments:

*Fill out all form fields before signing!

Name		 	Organization			Title			Signature 
 
_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________
 
_________________________________________________________________________________________________________________

_________________University of Missouri Commissioning Authority