# Project:

Columbia, MO 65211-3200

PHONE (573) 882-1133

FAX (573) 882-1175

Date:

# Medium Voltage Switchgear Construction Checklist (over 500 kVA)

| Project: |  |
| --- | --- |

| Date: |  |
| --- | --- |
| Building: |  |
| Location: |  |

## Submittal / Approvals

Submittal. The above equipment and systems integral to them are complete and ready for functional testing. The checklist items are complete and have been checked off only by parties having direct knowledge of the event, as marked below, respective to each responsible contractor. This construction checklist is submitted for approval, subject to an attached list of outstanding items yet to be completed. A Statement of Correction will be submitted upon completion of any outstanding areas. None of the outstanding items preclude safe and reliable functional tests being performed.		 List attached.

| Electrical Contractor | Date | General Contractor | Date |
| --- | --- | --- | --- |

Construction checklist items are to be completed as part of startup & initial checkout, preparatory to performing test procedures.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- If this form is not used for documenting, one of similar rigor shall be used.

- Contractors assigned responsibility for sections of the checklist shall be responsible to see that checklist items by their subcontractors are completed and checked off.

Approvals. This filled-out checklist has been reviewed. Its completion is approved with the exceptions noted below.

| Commissioning Authority | Date | Owner’s Representative | Date |
| --- | --- | --- | --- |

| Switchgear Information |  |  |  |
| --- | --- | --- | --- |
| Equipment Tag |  | Location |  |
| System (Circle one) | Power or Lighting | 208-120 or 480-277 | Normal or Emergency |
| Manufacturer |  | Model Number |  |
| Serial Number |  | Short Circuit Capacity |  |
| Volts/Phase Rating |  | Main Bus Amperage |  |
| Service Area |  | Other |  |
| Comments: |  |  |  |

| Associated Checklists |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Transformer |  | Other |  | Other |  |
| Comments: |  |  |  |  |  |

| Requested documentation submitted | Rec’d | Comments |
| --- | --- | --- |
| Manufacturer’s cut sheets |  |  |
| Installation and startup manual and plan |  |  |
| O&M manuals |  |  |
| Factory test results |  |  |
| Sequences and control strategies |  |  |
| Warranty Certificate |  |  |
| Comments: |  |  |

| Switchgear Enclosure/Cabinetry |  |  |  |
| --- | --- | --- | --- |
| Check if Acceptable; Provide comment if unacceptable |  | NA | Comment |
| Equipment installed per manufacturer’s instructions and specifications |  |  |  |
| Equipment installed agrees with shop drawings and specifications |  |  |  |
| Verify mounting, location and clearances are per plans and specifications |  |  |  |

| Inspect for physical, electrical and mechanical condition of equipment and cabinet. No damage evident |  |  |  |
| --- | --- | --- | --- |
| Inspect panels and doors for proper fit and alignment |  |  |  |
| Equipment labels permanently affixed |  |  |  |
| Panel is clean and clear of dust or dirt |  |  |  |
| Verify the application of manufacturer recommended torque values applied to bolted connections |  |  |  |
| Verify correct circuit breaker sizes and types per the specifications and manufacturer’s drawings |  |  |  |
| Seismic anchoring installed and functional where applicable (non- short circuiting) |  |  |  |
| Verify that all manufacturer control wiring between shipping splits is properly connected per manufacturer’s drawings and specifications |  |  |  |
| Inspect insulators, barriers and shields for damage or contamination |  |  |  |
| Verify that ground bus is properly bonded to enclosure, enclosure is grounded and resistance to ground meets grounding specifications |  |  |  |
| Verify three or four wire configuration |  |  |  |
| Metering transformer nameplate matches specified and approved transformer |  |  |  |
| Transformer installed per manufacturer’s instruction, plans and specifications |  |  |  |
| Inspect metering transformer cables and connections for defects or physical damage |  |  |  |
| Verify metering transformer connections are correct per the single line |  |  |  |
| Verify all grounding and shorting connections for the metering transformer are in place |  |  |  |
| Verify correct fusing for the metering transformer primary and secondary |  |  |  |
| Verify the metering transformer taps are in accordance with the manufacturer’s nameplate and specifications |  |  |  |
| Verify the vents and air inlets are free and unobstructed. Clean air filters installed (if required) |  |  |  |
| Megger test of bus – phase to phase and phase to ground. Test voltage per manufacturer’s recommendations |  |  |  |
| Hi-potential test of bus – phase to phase and phase to ground. Test voltage per manufacturer’s recommendations |  |  |  |
| Main Circuit Breaker |  |  |  |
| Installed per manufacturer’s instructions, plans and specifications |  |  |  |
| Verify all maintenance and service clearances are maintained |  |  |  |
| Verify no physical damage |  |  |  |
| Verify voltage and current rating of circuit breaker are per plans and specifications |  |  |  |

| Confirm correct application of manufacturer’s recommended lubricant |  |  |  |
| --- | --- | --- | --- |
| Verify that primary and secondary contact wipe dimensions are correct |  |  |  |
| Verify breakers are mounted securely and operates smoothly |  |  |  |
| Verify wire is properly installed and suitable size for breaker |  |  |  |
| Check cell fit and element alignment |  |  |  |
| Check racking mechanism |  |  |  |
| Megger test of circuit breaker – phase to phase and phase to ground. Test voltage per manufacturer’s recommendations |  |  |  |
| Inspect shutter operation |  |  |  |
| Verify that vacuum contact wipe dimensions are correct |  |  |  |
| Hi-potential test of circuit breaker – phase to phase and phase to ground. Test voltage per manufacturer’s recommendations |  |  |  |
| Feeder Circuit Breakers |  |  |  |
| Installed per manufacturer’s instructions, plans and specifications |  |  |  |
| Verify all maintenance and service clearances are maintained |  |  |  |
| Verify no physical damage |  |  |  |
| Verify voltage and current rating of circuit breaker are per plans and specifications |  |  |  |
| Confirm correct application of manufacturer’s recommended lubricant |  |  |  |
| Verify that primary and secondary contact wipe dimensions are correct |  |  |  |
| Verify breakers are mounted securely and operates smoothly |  |  |  |
| Verify wire is properly installed and suitable size for breaker |  |  |  |
| Check cell fit and element alignment |  |  |  |
| Check racking mechanism |  |  |  |
| Megger test of circuit breaker – phase to phase and phase to ground. Test voltage per manufacturer’s recommendations |  |  |  |
| Inspect shutter operation |  |  |  |
| Verify that vacuum contact wipe dimensions are correct |  |  |  |
| Hi-potential test of circuit breaker – phase to phase and phase to ground. Test voltage per manufacturer’s recommendations |  |  |  |

| Operational Checks |  |  |  |
| --- | --- | --- | --- |
| Check if Acceptable; Provide comment if unacceptable |  | NA | Comment |
| Control power energized to switchgear line-up |  |  |  |
| A full listing of all relay settings per the coordination study is provided and relays are programmed/set and tested |  |  |  |

# Project:

Columbia, MO 65211-3200

PHONE (573) 882-1133

FAX (573) 882-1175

Date:

| Electrically operated circuit breakers exercised in manual mode (electrically operated in test position and fully engaged position without main bus voltage applied) |  |  |  |
| --- | --- | --- | --- |
| All incoming cables are terminated and “ABC” phasing is correct. Terminations are torqued, checked, stress cones are properly grounded and exposed energized surfaces are insulated |  |  |  |
| Specified sequences of operation and operating schedules have been provided with all variations documented |  |  |  |
| Specified point-to-point checks have been completed and documentation record submitted for this system |  |  |  |

# Project:

Columbia, MO 65211-3200

PHONE (573) 882-1133

FAX (573) 882-1175

Date:

Comments:

*Fill out all form fields before signing!

Name		 	Organization			Title			Signature 
 
_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________

_________________________________________________________________________________________________________________
 
_________________________________________________________________________________________________________________

_________________University of Missouri Commissioning Authority